The SGV heavy duty grinder product has been designed to give you what you want, a durable submersible grinder pump and high end motor features, all designed to give you long life.  The pump features a vortex impeller with a cutter and cutter ring assembly designed to handle sewage and wastewater applications.  The motor features an epoxy resin sealed cable base, an overload “Auto-Cut” motor protector and oil lubricated double mechanical seals.

PRODUCT BULLETIN

MODEL SGV SUBMERSIBLE GRINDER

Bulletin 330SGV

Edition 2a

Material Specifications

| PART | CAST IRON FITTED |
| --- | --- |
| Casing | Cast Iron |
| Impeller | Cast Iron |
| Case Wear Ring | Cast Iron |
| Shaft | Stainless Steel |
| Motor Housing | Cast Iron |
| Mechanical Seal | Carbon/Ceramic Carbon/Si-Carbide |

MODEL SGV SPECIFICATIONS

Casing:  The casing is constructed of high tensile cast iron.   It is of the volute type, carefully and accurately proportioned to permit smooth flow and to convert high velocity energy of the fluid as it leaves the impeller into pressure. Suction and discharge nozzles are cast integral with the volute.  The casing has a vertical centerline discharge.  Necessary vent and drain openings are provided.

Impeller:  The impeller is of the vortex, end suction type, casted in one piece of cast iron material.  A cutter & cutter ring assembly is designed to cut through stringy solids in the pump fluid prior to it entering the casing assembly.  Vortex style impellers create a vortex within the casing minimizing wear on the impeller which leads to increased life.  All impellers are hydraulically and dynamically balanced prior to assembly and most impellers have pump out vanes standard on the back side of the imepller to reduce material from building up near the stuffing box.

Cutter Ring Assembly:   The cutter & cutter ring assembly are constructed out of corrosion resistant material and are designed to maserate solids as they enter the pump.  The SGF design features one lare cutter and several small cutters designed to cut through even the most aggressive solids.  Due to the aggressive duty required while in service, the entire assembly is hardened to 55-60 Rockwell C, ensuring long life.

Shaft:  The shaft is of high strength 420 stainless steel, ground to accurate dimensions and polished to a smooth surface.  It is designed for extra stiffness to avoid all critical speeds in operation.

Rear Cover:  The rear cover is constructed of cast iron or other specified material.  The rear cover houses the double  mechanical seal which has a Carbon/Cermanic motor side and Carbon/Silicon-Carbide pump side face arrangement.  Both mechanical seals are of the oil lubricated type to provide excellent lubricating fluid for the seal faces.  All seal hardware is located in the oil lubricated seal housing, eliminating potential issues with foreign matter clogging the mechanical seal springs.  An oil seal is located just outside of the seal chamber housing, adding a third seal to the pump assembly, which eliminated large solid matter from contacting the outside seal face assembly.

PRODUCT BULLETINMUNICIPALCOMMERCIALINDUSTRIAL

MODEL SGV SUBMERSIBLE Submersible Sewage, Heavy SolidsBuilding Waste,Residential,Process Solids, Industrial

GRINDERStorm WaterWaste

Motor: The motor housing frame is constructed of high tensile cast iron and provides support for the windings, shaft and bearing housing.  All American-Marsh submersible motors are air filled for ease in servicing, lower running temperatures and feature Class F insulation.  Air filled motors have the advantage of being easier to service due to the fact that the large volume of oil required for operation is not present.  Larger motor horsepowers feature a cooling jacket on the motor housing, which lowers operating temperatures and extends motor life.  These motors feature a motor overload design that protects the motor from high amperage draw, locked impeller and high temperature issues within the pumping assembly.  The cable base of the motor has a compression fitting, an epoxy sealed housing, stripped back motor leads (to prevent wicking of moisture) and o-ring construction to prohibit mousture from entering the motor housing.  On larger horsepower frame sizes, a moisture leakage detector is included standard for ultimate protection.

Easy Lift GRS (Guide Rail System):  American-Marsh’s Easy Lift GRS (Guide Rail System) allows the user to easily and efficiently remove and re-install a SBF Submersible Sewage Pump.  The Easy Lift GRS consists of  a discharge elbow, pump discharge coupling, two rails (not supplied) and a stainless steel lifting chain.  The Easy Lift GRS is a must for quickly servicing the pump and motor assembly.

Bulletin 330SGV

Edition 2a

SGV Sectional Drawing

| Item Number | Item Description | Num. Req. |  | Item Number | Item Description | Num. Req. |
| --- | --- | --- | --- | --- | --- | --- |
| 1A | Casing | 1 |  | 331G | Upper Housing Cover O-Ring | 1 |
| 2D | Mechanical Seal Bracket | 1 |  | 331L | Mechanical Seal Lubricant | 1 |
| 2E | Bearing Bracket | 1 |  | 331M | Upper Housing Cover O-Ring | 1 |
| 11C | Impeller | 1 |  | 331N | Motor Lead Base O-Ring | 1 |
| 11X | Radial Cutter | 1 |  | 331X | Mechanical Seal Moisture Sensor | 1 |
| 11Z | Radial Cutter Ring | 1 |  | 331XC | Mech. Seal Moisture Cable Base | 1 |
| 24A | Impeller Key | 1 |  | 331XD | Mech. Seal Moisture Sensor Cable | 1 |
| 24B | Impeller Locknut | 1 |  | 411D | Oil Plug | 2 |
| 27A | Impeller Lockwasher | 1 |  | 441A | Discharge Elbow | 1 |
| 81N | Outboard Bearing | 1 |  | 441B | Companion Flange | 1 |
| 81P | Inboard Bearing | 1 |  | 497A | Motor Housing | 1 |
| 81T | Inboard Bearing Thrust Plate | 1 |  | 497B | Upper Housing Cover | 1 |
| 104A | Oil Lip Seal Bushing | 1 |  | 497C | Motor Lead Base Cover | 1 |
| 104P | Oil Lip Seal | 1 |  | 497D | Motor Lead | 1 |
| 331A | Mechanical Seal (Motor Side) | 1 |  | 497F | Stator | 1 |
| 331B | Mechanical Seal (Pump Side) | 1 |  | 497G | Shaft (with Rotor) | 1 |
| 331C | Motor Housing O-Ring | 1 |  | 497H | Motor Overload Protection | 1 |
| 331D | Mechanical Seal Bracket O-Ring | 1 |  | 497X | Stainless Steel Eyehook | 3 |
| 331F | Casing O-Ring | 1 |  |  |  |  |

Recommended spare parts are in BOLD.