[image: image1.jpg]- A

AMERICAN-MARSH PUMPS




[image: image2.jpg]


[image: image3.jpg]1 351A 1B

104N 85N 8IN 2B 81P 104P 46A
1A
24A
41A
@l
Ilmﬂll
384B  359A >
411B
2E





PRODUCT BULLETIN

MODEL VF REGENERATIVE TURBINE
The newly re-designed American-Marsh model VF regenerative turbine pumps will handle ANY non-viscous, non-abrasive fluid – QUIETLY, EFFICIENTLY, & ECONOMICALLY.  Especially suited for many installations because internal parts can be removed without breaking any pipe connections or disturbing alignment.  Suction and discharge can be rotated to four different positions.  This style of pump can also handle fluid with entrained gas of up to 20%.  The newly redesigned pump now features renewable and replaceable channel rings and seal chamber.
Material Specifications

	PART
	CONSTRUCTION

	
	BRONZE FITTED
	IRON FITTED
	316SS FITTED

	Casing
	Cast Iron
	Cast Iron
	Cast Iron

	Casing Cover
	Cast Iron
	Cast Iron
	Cast Iron

	Impeller
	Bronze
	Bronze
	316 Stainless Steel

	Channel Rings
	Bronze
	Cast Iron
	316 Stainless Steel

	Shaft
	420 Stainless Steel
	420 Stainless Steel
	316 Stainless Steel

	Power Frame
	Cast Iron
	Cast Iron
	Cast Iron

	Bearing Cap
	Cast Iron
	Cast Iron
	Cast Iron

	Mechanical Seal
	Carbon/Ceramic/Buna
	Carbon/Ceramic/Buna
	Carbon/Caramic/Buna


MODEL VF SPECIFICATIONS

Casing:  The casing is of high tensile cast iron, or other specified material, accurately and carefully machined for maximum efficiency.  Inlet and outlet connections are cast integral with the casing.  Necessary openings are provided for venting and draining.  The casing features a removeable cover that will allow complete access to the internal components of the pump.  This will allow the inspection and/or replacement of the channel rings, the impeller, the seal chamber and the mechanical seal.  All of these components can be inspected and/or replaced without disturbing suction or discharge piping and without tearing apart the power frame.
Impeller:  The impeller is of cast bronze or other specified material,  machined all over with radial vanes accurately milled on both sides of the periphery.  Impellers are hydraulically balanced as fluid enters from two equal ports at the suction giving equal flow to both sides of the impeller, thus elimating end thrust.  The impeller has all surfaces machined and is perfectly balanced.

Channel Rings:  The new VF design features a floating impeller with replaceable and renewable channel rings.  The impeller, due to its hydraulically balanced design, floats in the center of the channel ring cavity.  As the channel rings wear and factory tolerances open up, the channel rings can be replaced and factory new performance can be accomplished.

Stuffing Box:  The seal chamber is of the FMI type, tapered and casted of bronze or other specified material.  A standard Carbon vs. Ceramic mechanical seal is supplied standard.  The seal chamber is so designed that it can be completely removed and replaced without replaceing other parts.  Also, the front side of the seal chamber has the channel ring incorporated for replacement of factory running tolerances.
Shaft:  The shaft is of 420 stainless steel and of ample proportions to safely transmit the maximum power and to avoid critical speeds over the entire operational speed range.
Power Frame:  The power frame is of cast iron designed so that it is not in contact with the pumped fluid.  The power frame now incorpates permanently lubricated ball bearings eliminating the need for re-greasing in the field.  

Ball Bearings:  The ball bearings are sealed, grease lubricated and of ample size to rigidly support the shaft.  The single row inboard bearing carries radial loads and is free to move in either direction.  The outboard bearing is of the deep groove, single row type to carry either radial loads or unbalanced thrust loads.

 


VF Sectional Drawing

	Item Number
	Item Description
	Num. Req.
	
	Item Number
	Item Description
	Num. Req.

	1A
	Casing
	1
	
	85N
	Outboard Bearing Cap
	1

	1B
	Casing Cover
	1
	
	104N
	Outboard Seal
	1

	2B
	Power Frame
	1
	
	104P
	Inboard Seal
	1

	2C
	Foot, Power Frame
	1
	
	125A
	Coupling Key
	1

	2D
	Rear Cover/Channel Ring
	1
	
	331B
	Mechanical Seal
	1

	2E
	Front Channel Ring
	1
	
	331D
	Mechanical Seal Locking Collar
	1

	11A
	Impeller
	1
	
	351A
	Casing Cover Gasket
	1

	24A
	Impeller Key
	1
	
	352A
	Rear Cover Gasket
	1

	41A
	Shaft
	1
	
	359A
	Bearing Housing Gasket
	1

	46A
	Water Slinger
	1
	
	384B
	Bearing Cap Capscrew
	1

	81N
	Outboard Bearing, Thrust
	1
	
	411B
	Plug, Drain
	1

	81P
	Inboard Bearing, Radial
	1
	
	
	
	


*Not shown in sectional.

Recommended spare parts are in BOLD.
PRODUCT BULLETIN			MUNICIPAL				COMMERCIAL			INDUSTRIAL


MODEL VF REGENERATIVE		High Pressure, Chemical Feed		HVAC, Booster,	Boiler Feed,		Process, Petrochemical,


TURBINE										Condensate Return, Seal Flush		Chemical Injection

















Bulletin 450


Edition 5














Bulletin 450


Edition 5














1
1

