PRODUCT BULLETIN

MODEL DEEP-WELL ENCLOSED LINESHAFT VERTICAL TURBINE

Deep-Well Enclosed Lineshaft Vertical Turbines

The American-Marsh Vertical Turbine pumps are designed for long, dependable life in many applications.  Modern processing methods require modern pumping equipment to satisfactorily handle the many and varied fluids used in the various industries.  American-Marsh Engineers, backed by over 125 years of manufacturing experience, have met this demand with the vertical turbines offered today.  We have incorporated in our design, ideas and suggestions from competent engineers from all sections of the country.

Material Specifications

| PART | CONSTRUCTION |
| --- | --- |
|  | BRONZE FITTED | ALL IRON | ALL BRONZE |
| Bowl Assembly | Cast Iron | Cast Iron | Bronze |
| Bowl Bearings | Bronze | Bronze | Bronze |
| Impeller(s) | Bronze | Cast Iron | Bronze |
| Bowl Shaft | 416 SS | 416 SS | 416 SS |
| Strainer | Galvanized Steel | Galvanized Steel | Galvanized Steel |
| Discharge Column | A53 Steel | A53 Steel | A53 Steel |
| Column Shaft | C1045 Steel | C1045 Steel | C1045 Steel |
| Column Bearings | Rubber | Rubber | Rubber |
| Discharge Head | Cast Iron | Cast Iron | Cast Iron |

PUMPING CONDITIONS:

Fluid to be Pumped:

Design Capacity (USGPM):

Differential Head (FEET):

Maximum RPM:

Minimum acceptable bowl efficiency, (%):

Viscosity (SSU):

Specific Gravity:

Suction Pressure (PSIG)

Temperature ((F):

MODEL DEEP WELL ENCLOSED LINESHAFT VT SPECIFICATIONS

Bowl Assembly:  The pump bowls shall be of close grained, cast iron ASTM A48 Class 30.  The water passages on bowl sizes 6” through 16” shall be lined with porcelain enamel or fusion epoxy lined to reduce friction loss, shall be free of blow holes, sand holes and other detrimental defects, and shall be accurately machined and fitted.  The impellers shall be of bronze (enclosed or semi-open) and dynamically balanced.  Impellers through 16” shall be securly fastened to the shaft with taper split bushings of steel.  Larger sizes shall be double-keyed.  Impellers shall be adjusted vertically by an external means.

The pump shaft shall be of A582 grade 416 stainless steel, turned, ground and polished.  It shall be supported by bronze bearings above and below each impeller.  The suction case bearing shall be grease lubricated and protected by a bronze sand collar.  The size of the shaft shall be no less than that determined by ANSI/AWWA Specifications E101, Section A4.3 paragraph 4.3.3.

Suction Pipe & Strainer:  The suction pipe shall be 10’ in length and of a size and weight at least equal to the outer column.  A galvanized cone type strainer shall be provided having a net inlet area equal to at least four times the suction pipe area.  The maximum opening size shall not be more than 75 percent on the minimum opening of the water passage through the bowl and impeller.

Column Assembly:  The lineshafts shall be of carbon steel ASTM A108 grade C1045 with 300 series stainless steel sleeves spaced at 10’ intervals for 1800 RPM and 5’ for 2200 RPM and over, turned and ground.  They shall be furnished in inter-changeable sections not over __________ feet in length.

The butting faces shall be machined square to the axis of the shaft, with maximum permissable axial misalignment on the thread axis with the shaft axis 0.002” in 6”.  The size of the shaft shall be no less than that determined by ANSI/AWWA-E101 Specifications Section 5.5 for C1045 lineshaft and shall be such that elongation due to hydraulic thrust will not exceed the axial clearance of the impellers in the pump bowls.  Maximum runout in 10’ shall not exceed 0.005”.

The lineshafts shall be provided with ASTM A269 grade 304 stainless steel threaded sleeves at the location of each lineshaft bearing.  The use of glues or any other means of securing the sleeve to the shaft, that is not field replaceable without the use of heat or special tools is not acceptable.  The lineshaft bearing shall be of 70 minimum shore hardness, neoprene, snap-in type, internally sprial grooved to flush out sand and other abrasives, mounted inside bronze bearing retainers held in position in the column pipe.  Bearing spacing shall not exceed 10’ for 1800 RPM of 5’ for 2200 RPM and above.

The outer column shall be either flanged or threaded of ASTM A53 grade B steel pipe of ASTM A120 interchangable sections not over 10’ in length for 2200 RPM and over with the ends of each section faced parallel and machined.  Threaded will have 8 straight threads per inch permitting the end to butt and insuring alignment when connected by standard mill steel coupling.  Flanged will be machined to accept bearing retainer in such a way as not to allow any movement of retainer after flanges are bolted securely together and to implement proper sealing of the column.  The weight of the column pipe shall be no less than that stated in ANSI/AWWA Specification E101, Section 5.1 “Standard Specifications for Discharge Column Pipe.”  The column size shall be such that friction loss will not exceed 5’ per 100’, based on the rated capacity of the pump.  If possible, the column size shall be such as to provide a velocity of not less than 5 feet per second at the rated capacity.

Top and bottom sections of column pipe on product lubricated pumps shall not exceed 5’ in length.

Discharge Head:  The discharge head shall be of close grain, cast iron, ASTM A48 class 30, free of sand holes and other defects, accurately machined and with a surface discharge.  Discharge flange shall be machined and drilled to ANSI standards for 125 lb. rating and shall be __________ inches nominal inside diameter.  The top of the discharge head shall have a rabbet fit to accurately locate the vertical hollow shaft driver, and have a diameter equal to the drive base diameter (BD) and less than __________ inches.

The standard cast iron stuffing box shall be rated for 125 PSI discharge pressure and shall be fitted with graphite acrylic packing.  It shall have a lantern ring or grease chamber placed as required below the top packing ring.  Throttle bearing shall be bronze with stainless steel bolting and with brass or stainless steel adjusting nuts.  Sealing between the stuffing box and the discharge head shall be accomplished by means of an o-ring.

If the discharge pressure exceeds 125 PSI, a high pressure bypass style packing box shall be supplied with a minimum of six rings of packing and two lantern rings and a bypass to sump.

If the setting is greater than 50’ and a non-pressure discharge, the pump shall be fitted with lubricated assembly consisting of galvanized steel tank and fittings with manual valve to lubricate the lineshaft bearings prior to startup.  If pumping into a pressurized system, a __________ inch solenoid prelube valve shall be supplied for __________ volts, 50 or 60 hertz, and the motor starter shall be fitted with a time delay relay to open prior to pump startup.

A unit which requires a mechanical seal shall have a housing bolted to the head with an o-ring seal.  The housing shall have a lower bronze throttle bushing.  The housing seal chamber shall accommodate a single sleeved (balanced/unbalanced) mechanical seal suitable for the maximum pressure developed by the pump of __________ PSI and temperature __________(F maximum.  Seal materials shall be compatible with the liquid pumped.  A balanced seal shall be mounted on a shaft sleeve.  The shaft supplied shall be one-piece bowl, line and head-shaft where practical of 416 stainless steel material.

The top lineshaft shall be of ASTM A582 grade 416 stainless steel  and shall not exceed 126” in length.  Impeller adjustment shall be provided at the top of the headshaft by means of adjusting nut which shall be positively locked in position.

Motor:  The electric motor shall be vertical hollow shaft __________ RPM., three phase (50 or 60 Hz) __________ volts with a non-reverse ratchet, P-base, squirrel cage induction design.  Enclosure shall meet NEMA weather protected type type 1 design with stainless steel screens to prevent entrance of rodents.  Motor shall have Class B or Class F insulation with temperature rise as specified by NEMA standards for class insulation used and shall have a 1.15 service factor.

Thrust bearing shall be chosen to handle the continuous down thrust as specified by the pump manufacturer with an AFBMA B-10 one-year minimum or five year average life under design conditions.  Provisions shall be made for momentary upthrust equal to 30 percent of rated down thrust.  The motor rating shall be such that at design it will not be loaded beyond nameplate rating and at no place on the pump curve shall the loading exceed the service factor.

OPEN LINESHAFT TURBINE PUMP SECTIONALS

ENCLOSED LINESHAFT TURBINE PUMP SECTIONALS

DEEP WELL VERTICAL TURBINE SECTIONAL DRAWING

| Item Number | Item Description |  | Item Number | Item Description |
| --- | --- | --- | --- | --- |
| 1 | Discharge Head |  | 70 | Oil Lubricated O/C Section (10’ 0” long) TBE |
| 2 | Head Column Flange |  | 71 | I/C Section (5’ 0” long) |
| 3 | Head Column Flange Gasket |  | 72 | Oil Lubricated L/S Section (10’ 0” long) |
| 4 | Studs |  | 73 | Oil Lubricated O/C Section (5’ 0” long) TBE |
| 5 | Nuts |  | 74 | Oil Lubricated L/S Section (5’ 0” long) TBE |
| 6 | Head Discharge Flange |  | 75 | I/C Stabilizing Spider |
| 7 | Head Discharge Flange Gasket |  | 76 | Water Lubricated O/C Section |
| 8 | Discharge Flange Assembly Cap Screws |  | 77 | Water Lubricated O/C Section |
| 9 | Discharge Flange Assembly Nuts |  | 78 | Water Lubricated L/S Bearing Spider |
| 10 | Head Discharge Flange Assembly Studs |  | 79 | Water Lubricated L/S Bearing |
| 11 | Head Discharge Flange Assembly Nuts |  | 80 | Water Lubricated L/S Sleeve |
| 14 | Head Packing Housing with Bearing |  | 81 | Water Lubricated L/S Extension (3’ 9-7/8” long) |
| 15 | O-Ring |  | 82 | Water Lubricated L/S Section (5’ 0” long) |
| 16 | Head Packing Housing Cap Screws |  | 83 | Water Lubricated L/S Section (10’ 0” long) |
| 17 | Oil Lubricated Headshaft |  | 84 | Water Lubricated Bowl Shaft |
| 18 | Water Lubricated Headshaft |  | 85 | Oil Lubricated Bowl Shaft |
| 18A | Top Shaft |  | 88 | Oil Lubricated Discharge Case |
| 19 | Headshaft Flinger |  | 89 | Oil Lubricated Discharge Case Bearing |
| 20 | Headshaft Adjusting Nut |  | 90 | Water Lubricated Case Bearing |
| 22 | Packing (Set) |  | 91 | Water Lubricated Case Bearing |
| 23 | Packing Follower |  | 93 | Water Lubricated Case Bearing |
| 25 | Head Packing Housing Grease Fittings |  | 94 | Sand Cap Set Screws |
| 26 | Packing Follower Studs |  | 96 | Shaft Seal |
| 27 | Packing Follower Retainer Nuts |  | 97 | I/C Adapter Coupling |
| 28 | Adapter Flange |  | 101 | Top Bowl Assembly |
| 29 | Adapter Flange O-Ring |  | 102 | Top Bowl Bearing |
| 30 | Adapter Flange Assembly Cap Screws |  | 103 | Bowl Assembly (Enclosed Type) |
| 31 | Oil Lubricated Headshaft Bearing |  | 104 | Bowl Bearing |
| 32 | Water Lubricated Headshaft Bearing |  | 105 | Bowl Assembly (Semi-Open Type) |
| 33 | Water Lubricated Headshaft Bearing |  | 106 | Impeller (Enclosed Type) |
| 34 | Adjusting Nut Machine Screw |  | 107 | Impeller (Semi-Open Type) |
| 40 | I/C Tension Nut |  | 108 | Taper Lock |
| 41 | Tension Nut Set Screw |  | 109 | Suction Case Assembly (Enclosed Type) |
| 42 | I/C Seal Ring |  | 110 | Suction Case Bearing |
| 43 | I/C Seal Ring Nut |  | 111 | Suction Case Assembly |
| 44 | Headshaft Bearing Assembly Cap Screws |  | 113 | Suction Case End Plug |
| 45 | Headshaft Bearing Dust Seal |  | 114 | Suction Case Sand Cap |
| 49 | Solenoids Valve |  | 115 | Optional Set Screws for Brass Sand Cap |
| 53 | Vented Sight Drip Valve |  | 116 | Bowl Suction Flange |
| 54 | Tubing for Oil Lubrication |  | 117 | Bowl Assembly Cap Screws |
| 55 | Oil Line Connector for Headshaft Bearing |  | 119 | Suction Bell (Optional) |
| 59 | Oil Level Sight Glass |  | 124 | Oil Lubricated O/C Section (20’ 0” long) |
| 63 | 2’ Long O/C Adapter Nipple TBE Top Section |  | 125 | Oil Lubricated L/S Section (20’ 0” long) |
| 64 | Inner Column Adapter 2’ 4” Long Stretch Nipple |  | 126 | Vented Toggle Valve |
| 65 | Oil Lubricated Lineshaft Bearing |  | 149 | Oil Lubricated O/C Assembly T&C (10’ 0” long) |
| 66 | Oil Lubricated Lineshaft Adapter Bearing |  | 150 | Oil Lubricated O/C Assembly T&C (5’ 0” long) |
| 67 | Shaft Coupling |  | 151 | Oil Lubricated O/C Assembly T&C (20’ 0” long) |
| 68 | Shaft Adapter Coupling |  | 152 | Water Lubricated O/C Asmbly T&C (10’ 0” long) |
| 69 | O/C Coupling |  | 153 | Water Lubricated O/C Asmbly T&C (5’ 0” long) |

Recommended spare parts are in BOLD.

DEEP WELL ENCLOSED LINESHAFT VERTICAL TURBINE

# Text boxes

PRODUCT BULLETIN			MUNICIPAL				COMMERCIAL			INDUSTRIAL

MODEL VERTICAL TURBINE		Quench Water, Filtration, Transfer,		Booster, Supply Water			Process, Petrochemical,

Filter Backwash, Circulation, Well							Cargo Transfer

- Your Local Authorized Distributor -

Pumps...and Pumps Only...Since 1873

Bulletin 480DWVT

Edition 1

| MATERIALS OF CONSTRUCTION |
| --- |
| BOWL | IMPELLER |
| BOWL SHAFT | SHAFT COUPLING |
| BOWL BEARINGS | SHAFT BEARINGS |
| STRAINER | BOWL W/R |
| IMPELLER W/R | COLUMN PIPE |
| LINESHAFT | PACKING |
| BASE PLATE | DISCHARGE HEAD |
| PUMP |
| TYPE | DISCHARGE HEAD |
| SUCTION | DISCHARGE |
| LINESHAFT | COLUMN |
| LUBRICATION | MODEL |
| STAGE | GPM |
| TDH | TRIM |
| RPM | BHP |
| MOTOR |
| MAKE | TYPE |
| ENCLOSURE | NRR |
| SRC | HP |
| RPM | PHASE |
| HERTZ | VOLTAGE |
| FRAME NO. | TYPE COUPLING |
| OTHER SPECIFICATIONS |
| DRAWING NO. | SERIAL NO. |
| FLUID | SPECIFIC GRAVITY |
| VISCOSITY | TEMPERATURE |
| PH | NO. UNITS REQUIRED |
| CUSTOMER |
| ADDRESS |
| CITY | ST | ZIP |
| TEL. ( ) | FAX. ( ) |
| REP. |
| SUPPLIER |
| SALESMAN |

Sales & Marketing:  185 Progress Road ( Collierville, Tennessee ( 38017

Manufacturing:  185 Progress Road ( Collierville, Tennessee ( 38017

Phone:  (800) 888-7167

Fax:  (901) 860-2323

Bulletin 480DWVT

Edition 1

Bulletin 480DWVT

Edition 1

Bulletin 480DWVT

Edition 1

Bulletin 480DWVT

Edition 1

Bulletin 480DWVT

Edition 1